## Table 1
Table 1 | [8 empty] | Table 2
Holyrood Fuel Conversion Rate | [8 empty] | Holyrood Fuel Conversion Rate
Regression Analysis | [8 empty] | Regression
Month | Year | Gross Average Unit Load (KW) | Running Heat Content (BTU/bbl) | Consumption Rate (Bbl/Hr) | Actual (kWh/Bbl) | Regression Consumption Rate (Bbl/Hr) | Regression (kWh/Bbl) | Line No |  |  | `
Jan | 2011 | 77675.7659 | 153231.6667 | 121.7031 | 638.24 | 123.6441 | 628.2205 |  | SUMMARY OUTPUT
Feb | 2011 | 85344.0818 | 153400.8333 | 131.9298 | 646.89 | 134.3045 | 635.4521
Mar | 2011 | 84075.371 | 155007.5 | 129.9324 | 647.07 | 131.3012 | 640.3245 |  | Regression Statistics
Apr | 2011 | 75640.2274 | 156505 | 117.2026 | 645.38 | 118.2981 | 639.4037 | 1 | Multiple R | 0.99103
May | 2011 | 72993.7219 | 155125.8333 | 115.7859 | 630.42 | 115.6205 | 631.3216 | 2 | R Square | 0.98215
Jun | 2011 | 71341.7106 | 153958.3333 | 113.9371 | 626.15 | 114.1816 | 624.8092 | 3 | Adjusted R Square | 0.9814
Oct | 2011 | 71769.8269 | 153824.1667 | 111.4871 | 643.75 | 114.8857 | 624.7066 | 4 | Standard Error | 2.5858
Nov | 2011 | 81672.666 | 153938.3333 | 126.0984 | 647.69 | 128.7315 | 634.4418 | 5 | Observations | 51
Dec | 2011 | 80564.5153 | 154179.1667 | 122.5726 | 657.28 | 126.9898 | 634.417
Jan | 2012 | 84167.5188 | 155070.8333 | 130.827 | 643.35 | 131.3828 | 640.6281 |  | ANOVA
Feb | 2012 | 85815.4155 | 155043.3333 | 131.6046 | 652.07 | 133.7221 | 641.7444 |  |  | df | SS | MS | F | Significance F
Mar | 2012 | 88363.3485 | 154738.3333 | 136.3737 | 647.95 | 137.5381 | 642.4644 | 6 | Regression | 2 | 17655.1508 | 8827.5754 | 1320.1984 | 1.1014e-42
Apr | 2012 | 82420.4978 | 154955.8333 | 129.1513 | 638.17 | 129.0121 | 638.8587 | 7 | Residual | 48 | 320.9545 | 6.6866
May | 2012 | 79935.6731 | 153499.1667 | 128.4912 | 622.11 | 126.6208 | 631.2999 | 8 | Total | 50 | 17976.1053
Jun | 2012 | 80683.3497 | 153380 | 128.7329 | 626.75 | 127.763 | 631.5077
Oct | 2012 | 68480.2116 | 153380 | 111.4968 | 614.19 | 110.5943 | 619.2022 |  |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
Nov | 2012 | 87972.0167 | 154231.6667 | 135.9187 | 647.24 | 137.3718 | 640.3937 | 9 | Intercept | 130.5582 | 25.6668 | 5.0866 | 5.9976e-06 | 78.9516 | 182.1648 | 78.9516 | 182.1648
Dec | 2012 | 92416.7887 | 154699.1667 | 145.2204 | 636.39 | 143.2707 | 645.0503 | 10 | Average Unit Load (kW) | 0.0014069 | 2.751e-05 | 51.1423 | 1.5909e-43 | 0.0013516 | 0.0014622 | 0.0013516 | 0.0014622
Jan | 2013 | 114416.8428 | 151527.5 | 176.6946 | 647.54 | 176.628 | 647.7843 | 11 | Heat Content (BTU/bbl) | -0.00075831 | 0.00016782 | -4.5187 | 4.0615e-05 | -0.0010957 | -0.0004209 | -0.0010957 | -0.0004209
Feb | 2013 | 116354.1667 | 152965.8333 | 180.1148 | 646 | 178.263 | 652.7109
Mar | 2013 | 88436.6404 | 153626.6667 | 139.2659 | 635.02 | 138.4842 | 638.6044 |  | Calculation of 2018 and 2019 Test Year Conversion Rate:
Apr | 2013 | 83883.4579 | 153191.6667 | 134.1384 | 625.35 | 132.4081 | 633.5219 |  |  | 2018 | 2019
May | 2013 | 77727.4506 | 153475.8333 | 125.3911 | 619.88 | 123.5317 | 629.2107 | 12 | Unit net average loading (kW) | 122244.1358 | 122220.815
Jun | 2013 | 73148.4712 | 153388.3333 | 122.5637 | 596.82 | 117.1558 | 624.3692 | 13 | Fuel Heating Content (BTU/US gal) | 152400 | 152400
Oct | 2013 | 66210.2513 | 153661.6667 | 108.3194 | 611.25 | 107.187 | 617.7077 | 14 | Station Service Factor | 6.193% | 6.193%
Nov | 2013 | 79102.9648 | 153368.3333 | 124.1824 | 636.99 | 125.5484 | 630.0594 | 15 | Unit gross average loading (kW) | 130314.8443 | 130289.9838 | Line 12 / (1 - Line 14)
Dec | 2013 | 101524.5223 | 152492.5 | 156.7898 | 647.52 | 157.7578 | 643.5467 | 16 | Fuel consumtion rate (bbl/hour) | 198.3335 | 198.2985 | Line 9 + (Line 15 x Line 10) + (Line 13 x Line 11)
Table 1 | [7 empty] | 17 | Net fuel conversion factor (kWh/bbl) | 616.3564 | 616.3475 | Line 12 / Line 16
Holyrood Fuel Conversion Rate
Regression Analysis
Month | Year | Gross Average Unit Load (KW) | Running Heat Content (BTU/bbl) | Consumption Rate (Bbl/Hr) | Actual (kWh/Bbl) | Regression Consumption Rate (Bbl/Hr) | Regression (kWh/Bbl)
Jan | 2014 | 93025.8619 | 150413.3333 | 152.0006 | 612.01 | 147.3776 | 631.2077 |  |  |  |  | Figure 1
Feb | 2014 | 108111.1654 | 151743.3333 | 169.8873 | 636.37 | 167.5928 | 645.0825 |  | Regression Correlation Chart
Mar | 2014 | 98353.4067 | 150900 | 153.5405 | 640.57 | 154.5039 | 636.5754 |  | Holyrood Fuel Consumption Rate vs Average Gross Unit Loading
Apr | 2014 | 83669.7248 | 148227.5 | 134.0839 | 624.01 | 135.8718 | 615.7989 |  |  |  |  | 2011 to 2015
May | 2014 | 84570.3431 | 149898.3333 | 137.7569 | 613.91 | 135.8719 | 622.427
Jun | 2014 | 71872.8634 | 150054.1667 | 116.254 | 618.24 | 117.8895 | 609.6632
Jul | 2014 | 69458.7608 | 148671.6667 | 117.5514 | 590.88 | 115.5414 | 601.1592
Aug | 2014 | 70241.9355 | 149225 | 115.8592 | 606.27 | 116.2236 | 604.3687
Sep | 2014 | 70268.9158 | 152232.5 | 119.566 | 587.7 | 113.981 | 616.4969
Oct | 2014 | 73694.7995 | 151903.3333 | 122.8533 | 599.86 | 119.0505 | 619.0212
Nov | 2014 | 86012.7247 | 150550 | 138.7817 | 619.77 | 137.4071 | 625.9702
Dec | 2014 | 93017.2397 | 149735.8333 | 147.3587 | 631.23 | 147.8792 | 629.0082
Jan | 2015 | 106955.7968 | 149673.3333 | 168.1166 | 636.2 | 167.537 | 638.4011
Feb | 2015 | 101290.7129 | 149880 | 157.5087 | 643.08 | 159.41 | 635.4102
Mar | 2015 | 101884.4868 | 150878.3333 | 157.0401 | 648.78 | 159.4883 | 638.8211
Apr | 2015 | 84191.1 | 151685 | 132.4176 | 635.8 | 133.9835 | 628.3692
May | 2015 | 75849.37 | 148969.1667 | 120.5432 | 629.23 | 124.3068 | 610.1786
Jun | 2015 | 70307.8381 | 148514.1667 | 109.9041 | 639.72 | 116.8554 | 601.6653
Jul | 2015 | 72123.6559 | 148912.5 | 116.1636 | 620.88 | 119.108 | 605.5314
Aug | 2015 | 68218.8162 | 148912.5 | 117.6755 | 579.72 | 113.6143 | 600.4424
Sep | 2015 | 68330.4647 | 150049.1667 | 116.7583 | 585.23 | 112.9094 | 605.1796
Oct | 2015 | 82073.8813 | 149692.5 | 132.2514 | 620.59 | 132.5157 | 619.3522
Nov | 2015 | 111655.9056 | 151990 | 174.5442 | 639.7 | 172.3929 | 647.6828
Dec | 2015 | 106509.8369 | 152513.3333 | 163.9218 | 649.76 | 164.7559 | 646.4704
Sorted Values: DO NOT PRINT
Month | Year | Gross Average Unit Load (KW) | Running Heat Content (BTU/bbl) | Consumption Rate (Bbl/Hr) | Actual (kWh/Bbl) | Regression Consumption Rate (Bbl/Hr) | Regression (kWh/Bbl)
Oct | 2013 | 66210.2513 | 153661.6667 | 108.3194 | 611.25 | 107.187 | 617.7077
Aug | 2015 | 68218.8162 | 148912.5 | 117.6755 | 579.72 | 113.6143 | 600.4424
Sep | 2015 | 68330.4647 | 150049.1667 | 116.7583 | 585.23 | 112.9094 | 605.1796
Oct | 2012 | 68480.2116 | 153380 | 111.4968 | 614.19 | 110.5943 | 619.2022
Jul | 2014 | 69458.7608 | 148671.6667 | 117.5514 | 590.88 | 115.5414 | 601.1592
Aug | 2014 | 70241.9355 | 149225 | 115.8592 | 606.27 | 116.2236 | 604.3687
Sep | 2014 | 70268.9158 | 152232.5 | 119.566 | 587.7 | 113.981 | 616.4969
Jun | 2015 | 70307.8381 | 148514.1667 | 109.9041 | 639.72 | 116.8554 | 601.6653
Jun | 2011 | 71341.7106 | 153958.3333 | 113.9371 | 626.15 | 114.1816 | 624.8092
Oct | 2011 | 71769.8269 | 153824.1667 | 111.4871 | 643.75 | 114.8857 | 624.7066
Jun | 2014 | 71872.8634 | 150054.1667 | 116.254 | 618.24 | 117.8895 | 609.6632
Jul | 2015 | 72123.6559 | 148912.5 | 116.1636 | 620.88 | 119.108 | 605.5314
May | 2011 | 72993.7219 | 155125.8333 | 115.7859 | 630.42 | 115.6205 | 631.3216
Jun | 2013 | 73148.4712 | 153388.3333 | 122.5637 | 596.82 | 117.1558 | 624.3692
Oct | 2014 | 73694.7995 | 151903.3333 | 122.8533 | 599.86 | 119.0505 | 619.0212
Apr | 2011 | 75640.2274 | 156505 | 117.2026 | 645.38 | 118.2981 | 639.4037
May | 2015 | 75849.37 | 148969.1667 | 120.5432 | 629.23 | 124.3068 | 610.1786
Jan | 2011 | 77675.7659 | 153231.6667 | 121.7031 | 638.24 | 123.6441 | 628.2205
May | 2013 | 77727.4506 | 153475.8333 | 125.3911 | 619.88 | 123.5317 | 629.2107
Nov | 2013 | 79102.9648 | 153368.3333 | 124.1824 | 636.99 | 125.5484 | 630.0594
May | 2012 | 79935.6731 | 153499.1667 | 128.4912 | 622.11 | 126.6208 | 631.2999
Dec | 2011 | 80564.5153 | 154179.1667 | 122.5726 | 657.28 | 126.9898 | 634.417
Jun | 2012 | 80683.3497 | 153380 | 128.7329 | 626.75 | 127.763 | 631.5077
Nov | 2011 | 81672.666 | 153938.3333 | 126.0984 | 647.69 | 128.7315 | 634.4418
Oct | 2015 | 82073.8813 | 149692.5 | 132.2514 | 620.59 | 132.5157 | 619.3522
Apr | 2012 | 82420.4978 | 154955.8333 | 129.1513 | 638.17 | 129.0121 | 638.8587
Apr | 2014 | 83669.7248 | 148227.5 | 134.0839 | 624.01 | 135.8718 | 615.7989
Apr | 2013 | 83883.4579 | 153191.6667 | 134.1384 | 625.35 | 132.4081 | 633.5219
Mar | 2011 | 84075.371 | 155007.5 | 129.9324 | 647.07 | 131.3012 | 640.3245
Jan | 2012 | 84167.5188 | 155070.8333 | 130.827 | 643.35 | 131.3828 | 640.6281
Apr | 2015 | 84191.1 | 151685 | 132.4176 | 635.8 | 133.9835 | 628.3692
May | 2014 | 84570.3431 | 149898.3333 | 137.7569 | 613.91 | 135.8719 | 622.427
Feb | 2011 | 85344.0818 | 153400.8333 | 131.9298 | 646.89 | 134.3045 | 635.4521
Feb | 2012 | 85815.4155 | 155043.3333 | 131.6046 | 652.07 | 133.7221 | 641.7444
Nov | 2014 | 86012.7247 | 150550 | 138.7817 | 619.77 | 137.4071 | 625.9702
Nov | 2012 | 87972.0167 | 154231.6667 | 135.9187 | 647.24 | 137.3718 | 640.3937
Mar | 2012 | 88363.3485 | 154738.3333 | 136.3737 | 647.95 | 137.5381 | 642.4644
Mar | 2013 | 88436.6404 | 153626.6667 | 139.2659 | 635.02 | 138.4842 | 638.6044
Dec | 2012 | 92416.7887 | 154699.1667 | 145.2204 | 636.39 | 143.2707 | 645.0503
Dec | 2014 | 93017.2397 | 149735.8333 | 147.3587 | 631.23 | 147.8792 | 629.0082
Jan | 2014 | 93025.8619 | 150413.3333 | 152.0006 | 612.01 | 147.3776 | 631.2077
Mar | 2014 | 98353.4067 | 150900 | 153.5405 | 640.57 | 154.5039 | 636.5754
Feb | 2015 | 101290.7129 | 149880 | 157.5087 | 643.08 | 159.41 | 635.4102
Dec | 2013 | 101524.5223 | 152492.5 | 156.7898 | 647.52 | 157.7578 | 643.5467
Mar | 2015 | 101884.4868 | 150878.3333 | 157.0401 | 648.78 | 159.4883 | 638.8211
Dec | 2015 | 106509.8369 | 152513.3333 | 163.9218 | 649.76 | 164.7559 | 646.4704
Jan | 2015 | 106955.7968 | 149673.3333 | 168.1166 | 636.2 | 167.537 | 638.4011
Feb | 2014 | 108111.1654 | 151743.3333 | 169.8873 | 636.37 | 167.5928 | 645.0825
Nov | 2015 | 111655.9056 | 151990 | 174.5442 | 639.7 | 172.3929 | 647.6828
Jan | 2013 | 114416.8428 | 151527.5 | 176.6946 | 647.54 | 176.628 | 647.7843
Feb | 2013 | 116354.1667 | 152965.8333 | 180.1148 | 646 | 178.263 | 652.7109