## Sheet1
SUMMARY OF POWER GENERATION AND DISTRIBUTION
MONTHLY POWER REPORT (kWhrs)
Month of: June 2018 |  | Island Interconnected System
| MONTH | MONTH | 12 M-T-D | 12 M-T-D | 12 M-T-D Delta | CHANGE | Calendar YTD
GENERATION | LAST YEAR | THIS YEAR | LAST YEAR | THIS YEAR | KWHRS | % | THIS YEAR
Bay D'Espoir | 127724160 | 166435200 | 2653935360 | 2626256640 | -27678720 | -1.043% | 1536393600
Hinds Lake | 34401888 | 41238360 | 365317230 | 311020092 | -54297138 | -14.86% | 184404168
Upper Salmon | 39607965 | 39978675 | 569926890 | 564900030 | -5026860 | -0.882% | 317644515
Cat Arm | 59787200 | 70385150 | 761538650 | 862107750 | 100569100 | 13.21% | 501369750
Paradise River | 831118 | 2242828 | 30236339 | 32100711 | 1864372 | 6.166% | 20791017
Granite Canal | 12308940 | 20255580 | 228951135 | 247678785 | 18727650 | 8.18% | 141770565
Mini Hydro Sites | 599700 | 322020 | 4096140 | 3045600 | -1050540 | -25.65% | 1469910
SUB TOTAL HYDRO GENERATION | 275260971 | 340857813 | 4614001744 | 4647109608 | 33107864 | 0.7176% | 2703843525
Holyrood Thermal | 68040000 | 42300000 | 1670500000 | 1471170000 | -199330000 | -11.93% | 714150000
GNP Diesel & Other Mobile | 11383 | 2333 | 665220 | 853729 | 188509 | 28.34% | 592585
Hardwoods GT | 288000 | 72000 | 3745000 | 4608000 | 863000 | 23.04% | 3312000
Holyrood CT | 341000 | 3147000 | 52236000 | 72955000 | 20719000 | 39.66% | 41290000
Holyrood Diesels | 2398 | 53674 | 576972 | 307354 | -269618 | -46.73% | 120707
Stephenville GT | 44683 | 273189.6 | 1583866.8 | 1358600.4 | -225266.4 | -14.22% | 1047661.2
SUB TOTAL THERMAL GENERATION | 68727464 | 45848196.6 | 1729307058.8 | 1551252683.4 | -178054375.4 | -10.3% | 760512953.2
SYSTEM GROSS GENERATION | 343988435 | 386706009.6 | 6343308802.8 | 6198362291.4 | -144946511.4 | -2.285% | 3464356478.2
STATION SERVICES
Bay D'Espoir | 329234 | 310480 | 4673263 | 4872534 | 199271 | 4.264% | 2780332
Hinds Lake | 73691 | 86850 | 1282670 | 1435871 | 153201 | 11.94% | 886440
Upper Salmon | 194500 | 243700 | 3451100 | 3542600 | 91500 | 2.651% | 2083100
Cat Arm | 130074 | -122989 | 1627050 | 1594353 | -32697 | -2.01% | 891903
Paradise River | 11700 | 23990 | 195720 | 229490 | 33770 | 17.25% | 129690
Granite Canal | 158297 | 75865 | 2300893 | 1040726 | -1260167 | -54.77% | 621804
Holyrood Thermal | 4303767 | 3277285 | 88354192 | 89859865 | 1505673 | 1.704% | 46155501
Stephenville GT | 140893 | 157295.6 | 1688149.2 | 1911863.3 | 223714.1 | 13.25% | 1021308.5
Hardwoods GT | 61414 | 74147.034 | 868887.92 | 923496.04 | 54608.12 | 6.285% | 529944.986
Mini Hydro Sites | 2475 | 1500 | 46046 | 43137 | -2909 | -6.318% | 27297
GNP Diesel | 53036 | 58563 | 851689 | 766353 | -85336 | -10.02% | 473321
TOTAL STATION SERVICES | 5459081 | 4186686.634 | 105339660.12 | 106220288.34 | 880628.22 | 0.836% | 55600641.486
SYNCHRONOUS CONDENSOR CONSUMPTION
Bay D'Espoir | 67400 | 30800 | 170500 | 243000 | 72500 | 42.52% | 73400
Cat Arm | 0 | 0 | 400000 | 200000 | -200000 | -50% | 100000
Hardwoods GT | 576000 | 288000 | 5256000 | 5256000 | 0 | 0% | 2304000
Stephenville GT | 485496 | 476373.6 | 4857883.2 | 6010160.4 | 1152277.2 | 23.72% | 2997792
TOTAL SYNC. CONDENSOR USE | 1128896 | 795173.6 | 10684383.2 | 11709160.4 | 1024777.2 | 9.591% | 5475192
SYSTEM NET GENERATION | 337400458 | 381724149.366 | 6227284759.48 | 6080432842.66 | -146851916.82 | -2.358% | 3403280644.714
Hydro Requested Nfld Power | 0 | 0 | 683135 | 831403 | 148268 | 21.7% | 550456
Hydro Requested Vale | 0 | 0 | 438418 | 198884 | -239534 | -54.64% | 108324
CBPP Secondary (including Capacity Assistance) | 1160867 | 676691.25 | 10026030.75 | 16413376.5 | 6387345.75 | 63.71% | 8150610.75
CBPP Exchanged/Transferred Energy (to NLH) | 0 | 0 | 0 | 0 | 0 | 0% | 0
Nalcor - Grand Falls and Bishop's Falls | 43215637 | 50771596 | 520885603 | 524199851 | 3314248 | 0.6363% | 288306251
Nalcor - Star Lake | 9694514 | 11786009 | 134414892 | 135024426 | 609534 | 0.4535% | 68187630
Rattle Brook | 2469305 | 2353032 | 14712358 | 14633304 | -79054 | -0.5373% | 7689137
CBPP CoGen | 7129324 | 6241956 | 65408064 | 73018742 | 7610678 | 11.64% | 36248744
Nalcor - Buchans | 0 | 0 | 0 | 0 | 0 | 0% | 0
St. Lawrence Wind | 7193607 | 7832899 | 101512820 | 104428519 | 2915699 | 2.872% | 59298285
Fermeuse Wind | 8884388 | 6489314 | 88748365 | 95300843 | 6552478 | 7.383% | 53391704
Maritime Link Imports | 0 | 4789482.9 | 0 | 31699023.4 | 31699023.4 | 0% | 31602396.4
New World Dairy | 0 | 233546 | 0 | 1375579 | 1375579 | 0% | 1375579
Soldiers Pond Imports | 0 | 3950998.0159 | 0 | 3950998.0159 | 3950998.0159 | 0% | 3950998.0159
TOTAL OTHER SOURCES | 79747642 | 95125524.1659 | 936829685.75 | 1001074948.9159 | 64245263.1659 | 6.858% | 558860115.1659
TOTAL NET GENERATION | 417148100 | 476849673.5319 | 7164114445.23 | 7081507791.5759 | -82606653.6541 | -1.153% | 3962140759.8799
|  |  | 12 M-T-D | 12 M-T-D | TO DATE | CHANGE | YTD
ENERGY DISTRIBUTION | LAST YEAR | THIS YEAR | LAST YEAR | THIS YEAR | KWHRS | % | THIS YEAR
Vale Newfoundland and Labrador Ltd. | 16643941 | 26840408 | 219290409 | 304926545.2153 | 85636136.2153 | 39.05% | 152433936
Praxair Canada Inc. | 2059100 | 4092483 | 40379027 | 45808754 | 5429727 | 13.45% | 23117356
Corner Brook Pulp & Paper Co. Ltd. | 903086 | -553282 | 41499560.75 | 19253036.25 | -22246524.5 | -53.61% | 10302357.75
Teck Resources Ltd. | 241090 | 228110.5 | 4358715.3 | 3045141.4 | -1313573.9 | -30.14% | 1705664.8
North Atlantic Refining Ltd. | 19961299 | 14736709 | 232202587 | 235773561 | 3570974 | 1.538% | 107996815
TOTAL INDUSTRY | 39808516 | 45344428.5 | 537730299.05 | 608807037.8653 | 71076738.8153 | 13.22% | 295556129.55
Newfoundland Power | 333307254 | 375210617 | 5926440576 | 5768661885 | -157778691 | -2.662% | 3272285132
Maritime Link Exports | 0 | 2450259.5 | 0 | 10785609.3 | 10785609.3 | 0% | 9596876.3
Rural Bulk Deliveries | 31518483 | 34700881 | 479984623 | 475101867 | -4882756 | -1.017% | 261919236
TOTAL UTILITY | 364825737 | 412361757.5 | 6406425199 | 6254549361.3 | -151875837.7 | -2.371% | 3543801244.3
CBP&P Exchanged/Transferred Energy Credit (from NLH) | 0 | 0 | 0 | 0 | 0 | 0% | 0
TOTAL ENERGY DISTRIBUTED | 404634253 | 457706186 | 6944155498.05 | 6863356399.1653 | -80799098.8847 | -1.164% | 3839357373.85
TRANSMISSION, TRANSFORMER LOSSES | 12513847 | 19143487.5319 | 219958947.18 | 218151392.4107 | -1807554.7693 | -0.8218% | 122783386.0299
| 3% | 4.015% | 3.07% | 3.081% |  |  | 3.099%
ISLAND PEAK MW | 1078.54 | 1202.52 | 1714.15 | 1647.86 | Established | 1714.47
ISLAND PEAK TIME | 16:57 | 8:03 | 7:13 | 16:42 | Record Peaks | 10:07
ISLAND PEAK DATE | 2017-06-05 | 2018-06-04 | 2017-02-08 | 2017-12-27 |  | 2014-02-10
Printed Date/Time: | 2018-11-16 | 43420.5119
Comments: | 2018-07-11-1000 Updates: Bay D'Espoir Generation, "LTA / LIL Imports" replaced with "Soldiers Pond Imports", CBPPL Adjustment Energy Credit, Added "Calendar YTD THIS YEAR" Column
2018-07-12-1000 Updates: Data Tab calculation updated to include Soldiers Pond in System Losses (no affect to the Reports Tab, or PDF version). Cat Arm SS is negative due to a meter reading correction
2018-06-01 | [5 empty] | H:\Operations\Monthly Reports\SPGD\2018 spgd\[spgd_2018_06.xls]PUB Qtr Input