## Overall Contingency Summary
Year | Baseline (or Alternative 4)
| EUE (MWh) | Total Fuel Consumption (L) | Fuel Price Forecast2 | Power Outage Costs ($)
2019 | 424.9725 | 130760.7721 | 1.347 | 176134.76
2020 | 645.1985 | 198522.6076 | 1.495 | 296791.2983
2021 | 849.4407 | 261366.3814 | 1.405 | 367219.7659
2022 | 855.2249 | 263146.1088 | 1.355 | 356562.9775
2023 | 863.9815 | 265840.4748 | 1.345 | 357555.4386
2024 | 872.8745 | 268576.7793 | 1.365 | 366607.3038 | CPV: | 5028361.2249
2025 | 881.9167 | 271358.9883 | 1.38 | 374475.4038
2026 | 891.028 | 274162.4522 | 1.405 | 385198.2454
2027 | 900.2305 | 276994.0046 | 1.435 | 397486.3966
2028 | 909.5139 | 279850.4333 | 1.455 | 407182.3805
2029 | 918.9401 | 282750.8048 | 1.48 | 418471.191
2030 | 925.3457 | 284721.7509 | 1.51 | 429929.8439
2031 | 935.0709 | 287714.109 | 1.535 | 441641.1573
2032 | 944.9121 | 290742.1845 | 1.565 | 455011.5188
2033 | 954.965 | 293835.3742 | 1.59 | 467198.2449
2034 | 961.7387 | 295919.595 | 1.62 | 479389.7439
2035 | 971.9579 | 299063.9821 | 1.65 | 493455.5705
2036 | 978.8328 | 301179.3193 | 1.68 | 505981.2565
2037 | 985.7492 | 303307.4402 | 1.705 | 517139.1855
2038 | 996.2753 | 306546.2315 | 1.735 | 531857.7117
2039 | 1003.4083 | 308741.0216 | 1.765 | 544927.9031
2040 | 1014.24 | 312073.8525 | 1.8 | 561732.9345
2041 | 1021.5716 | 314329.7219 | 1.835 | 576795.0397
2042 | 1032.7834 | 317779.5178 | 1.87 | 594247.6982
2043 | 1040.4337 | 320133.4362 | 1.91 | 611454.8632
2044 | 1051 | 323384.6154 | 1.945 | 628983.0769
NOTES: 1 - Assumed Generator Efficiency of 3.25 kWh/L 2 - As per Table 3.2 (Page 13) in the Labrador Expansion Study

## Altern 4 Conting Limits
Month | High Temp | L23/24 Rating | L23 | Limitation | L24 | Limitation | SC1 | Limitation | SC2 | Limitation | SC3 | Limitation | C1 | Limitation | C2 | Limitation | C3 | Limitation | T1 | Limitation | T2 | Limitation | T3 | Limitation | T8 | Limitation | T4 | Limitation | T5 | Limitation | T6 | Limitation | T7 | Limitation
|  |  |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt
Jan | -16 | 374.2612 | 296.01 | Voltage | 296.01 | Voltage | 358.6 | Voltage | 367.23 | Voltage | 367.23 | Voltage | 390.25 | Voltage | 408.4 | Voltage | 408.4 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Feb | -14 | 368.9666 | 296.01 | Voltage | 296.01 | Voltage | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Mar | -7 | 348.0352 | 290.9 | Thermal | 290.9 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Apr | 1 | 319.5416 | 276.03 | Thermal | 276.03 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
May | 10 | 281.657 | 250.64 | Thermal | 250.64 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Jun | 16 | 252.9716 | 229.53 | Thermal | 229.53 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Jul | 19 | 237.6002 | 217.47 | Thermal | 217.47 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Aug | 18 | 242.8002 | 221.74 | Thermal | 221.74 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Sep | 12 | 272.4 | 244.6 | Thermal | 244.6 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Oct | 4 | 307.5992 | 269.23 | Thermal | 269.23 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Nov | -4 | 337.9216 | 285.85 | Thermal | 285.85 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Dec | -13 | 366.205 | 296.44 | Voltage | 296.44 | Voltage | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Limitations
SC1/SC2/SC3 - Maximum voltage 1.05 pu, try and maximize this value, this will enable maximum VAR output from machines
Bus B13/B15 - Must be kept above 1.013 pu, can go higher but not lower