## Overall Contingency Summary
As per LAB-NLH-102, Attachment 2
Year | Increase Due to Data Centers |  |  | Year | Baseline (or Alternative 4) - NO DATA CENTERS |  |  |  | Year | Baseline (or Alternative 4) - DATA CENTERS
| EUE (MWh) | Total Fuel Consumption (L) | Power Outage Costs ($) |  | EUE (MWh) | Total Fuel Consumption (L) | Fuel Price Forecast2 | Power Outage Costs ($) |  | EUE (MWh) | Total Fuel Consumption (L) | Fuel Price Forecast2 | Power Outage Costs ($)
2019 | 108.7105 | 33449.3842 | 45056.3206 | 2019 | 316.262 | 97311.3879 | 1.347 | 131078.4395 | 2019 | 424.9725 | 130760.7721 | 1.347 | 176134.76
2020 | 145.5966 | 44798.9394 | 66974.4144 | 2020 | 499.6019 | 153723.6681 | 1.495 | 229816.8839 | 2020 | 645.1985 | 198522.6076 | 1.495 | 296791.2983
2021 | 174.2694 | 53621.3611 | 75338.0123 | 2021 | 675.1713 | 207745.0204 | 1.405 | 291881.7536 | 2021 | 849.4407 | 261366.3814 | 1.405 | 367219.7659
2022 | 173.0168 | 53235.9414 | 72134.7006 | 2022 | 682.208 | 209910.1675 | 1.355 | 284428.2769 | 2022 | 855.2249 | 263146.1088 | 1.355 | 356562.9775
2023 | 177.0692 | 54482.8222 | 73279.3959 | 2023 | 686.9124 | 211357.6526 | 1.345 | 284276.0427 | 2023 | 863.9815 | 265840.4748 | 1.345 | 357555.4386
2024 | 178.8832 | 55040.9887 | 75130.9495 | 2024 | 693.9913 | 213535.7907 | 1.365 | 291476.3543 | 2024 | 872.8745 | 268576.7793 | 1.365 | 366607.3038
2025 | 180.8265 | 55638.9139 | 76781.7012 | 2025 | 701.0902 | 215720.0744 | 1.38 | 297693.7027 | 2025 | 881.9167 | 271358.9883 | 1.38 | 374475.4038
2026 | 182.7977 | 56245.447 | 79024.8531 | 2026 | 708.2303 | 217917.0052 | 1.405 | 306173.3923 | 2026 | 891.028 | 274162.4522 | 1.405 | 385198.2454
2027 | 182.3473 | 56106.8721 | 80513.3614 | 2027 | 717.8832 | 220887.1325 | 1.435 | 316973.0352 | 2027 | 900.2305 | 276994.0046 | 1.435 | 397486.3966
2028 | 184.2594 | 56695.1904 | 82491.502 | 2028 | 725.2545 | 223155.2429 | 1.455 | 324690.8785 | 2028 | 909.5139 | 279850.4333 | 1.455 | 407182.3805
2029 | 188.7312 | 58071.1511 | 85945.3037 | 2029 | 730.2089 | 224679.6536 | 1.48 | 332525.8874 | 2029 | 918.9401 | 282750.8048 | 1.48 | 418471.191
2030 | 187.6591 | 57741.2506 | 87189.2883 | 2030 | 737.6866 | 226980.5004 | 1.51 | 342740.5556 | 2030 | 925.3457 | 284721.7509 | 1.51 | 429929.8439
2031 | 192.3817 | 59194.3547 | 90863.3344 | 2031 | 742.6892 | 228519.7543 | 1.535 | 350777.8229 | 2031 | 935.0709 | 287714.109 | 1.535 | 441641.1573
2032 | 194.6251 | 59884.6447 | 93719.469 | 2032 | 750.287 | 230857.5398 | 1.565 | 361292.0498 | 2032 | 944.9121 | 290742.1845 | 1.565 | 455011.5188
2033 | 197.0241 | 60622.8023 | 96390.2556 | 2033 | 757.9409 | 233212.5719 | 1.59 | 370807.9893 | 2033 | 954.965 | 293835.3742 | 1.59 | 467198.2449
2034 | 198.6815 | 61132.7774 | 99035.0994 | 2034 | 763.0572 | 234786.8176 | 1.62 | 380354.6445 | 2034 | 961.7387 | 295919.595 | 1.62 | 479389.7439
2035 | 201.2034 | 61908.7538 | 102149.4438 | 2035 | 770.7545 | 237155.2283 | 1.65 | 391306.1268 | 2035 | 971.9579 | 299063.9821 | 1.65 | 493455.5705
2036 | 200.3543 | 61647.49 | 103567.7832 | 2036 | 778.4784 | 239531.8293 | 1.68 | 402413.4733 | 2036 | 978.8328 | 301179.3193 | 1.68 | 505981.2565
2037 | 204.6875 | 62980.7641 | 107382.2028 | 2037 | 781.0617 | 240326.6761 | 1.705 | 409756.9827 | 2037 | 985.7492 | 303307.4402 | 1.705 | 517139.1855
2038 | 207.3917 | 63812.831 | 110715.2618 | 2038 | 788.8836 | 242733.4005 | 1.735 | 421142.4499 | 2038 | 996.2753 | 306546.2315 | 1.735 | 531857.7117
2039 | 206.5535 | 63554.9235 | 112174.44 | 2039 | 796.8548 | 245186.0981 | 1.765 | 432753.4631 | 2039 | 1003.4083 | 308741.0216 | 1.765 | 544927.9031
2040 | 212.0272 | 65239.1378 | 117430.4481 | 2040 | 802.2128 | 246834.7147 | 1.8 | 444302.4864 | 2040 | 1014.24 | 312073.8525 | 1.8 | 561732.9345
2041 | 211.2793 | 65009.0172 | 119291.5466 | 2041 | 810.2923 | 249320.7047 | 1.835 | 457503.4931 | 2041 | 1021.5716 | 314329.7219 | 1.835 | 576795.0397
2042 | 217.0486 | 66784.176 | 124886.409 | 2042 | 815.7349 | 250995.3418 | 1.87 | 469361.2892 | 2042 | 1032.7834 | 317779.5178 | 1.87 | 594247.6982
2043 | 219.224 | 67453.5383 | 128836.2581 | 2043 | 821.2097 | 252679.898 | 1.91 | 482618.6052 | 2043 | 1040.4337 | 320133.4362 | 1.91 | 611454.8632
2044 | 222 | 68307.6923 | 132858.4615 | 2044 | 829 | 255076.9231 | 1.945 | 496124.6154 | 2044 | 1051 | 323384.6154 | 1.945 | 628983.0769
NOTES: 1 - Assumed Generator Efficiency of 3.25 kWh/L 2 - As per Table 3.2 (Page 13) in the Labrador Expansion Study |  |  |  | NOTES: 1 - Assumed Generator Efficiency of 3.25 kWh/L 2 - As per Table 3.2 (Page 13) in the Labrador Expansion Study |  |  |  |  | NOTES: 1 - Assumed Generator Efficiency of 3.25 kWh/L 2 - As per Table 3.2 (Page 13) in the Labrador Expansion Study
|  | CPV: | 1047624.3489

## Altern 4 Conting Limits
Month | High Temp | L23/24 Rating | L23 | Limitation | L24 | Limitation | SC1 | Limitation | SC2 | Limitation | SC3 | Limitation | C1 | Limitation | C2 | Limitation | C3 | Limitation | T1 | Limitation | T2 | Limitation | T3 | Limitation | T8 | Limitation | T4 | Limitation | T5 | Limitation | T6 | Limitation | T7 | Limitation
|  |  |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt |  | Therm/Volt
Jan | -16 | 374.2612 | 296.01 | Voltage | 296.01 | Voltage | 358.6 | Voltage | 367.23 | Voltage | 367.23 | Voltage | 390.25 | Voltage | 408.4 | Voltage | 408.4 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Feb | -14 | 368.9666 | 296.01 | Voltage | 296.01 | Voltage | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Mar | -7 | 348.0352 | 290.9 | Thermal | 290.9 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Apr | 1 | 319.5416 | 276.03 | Thermal | 276.03 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
May | 10 | 281.657 | 250.64 | Thermal | 250.64 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Jun | 16 | 252.9716 | 229.53 | Thermal | 229.53 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Jul | 19 | 237.6002 | 217.47 | Thermal | 217.47 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Aug | 18 | 242.8002 | 221.74 | Thermal | 221.74 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Sep | 12 | 272.4 | 244.6 | Thermal | 244.6 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Oct | 4 | 307.5992 | 269.23 | Thermal | 269.23 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Nov | -4 | 337.9216 | 285.85 | Thermal | 285.85 | Thermal | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Dec | -13 | 366.205 | 296.44 | Voltage | 296.44 | Voltage | 364.4 | Voltage | 373 | Voltage | 373 | Voltage | 399.7 | Voltage | 406.1 | Voltage | 406.1 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 421.5 | Voltage | 419.5 | Voltage | 393.1 | Thermal | 393.1 | Thermal | 419.47 | Voltage | 416.5 | Voltage
Limitations
SC1/SC2/SC3 - Maximum voltage 1.05 pu, try and maximize this value, this will enable maximum VAR output from machines
Bus B13/B15 - Must be kept above 1.013 pu, can go higher but not lower