## Plexos Input
| Avalon Load | Avalon Load (Production) | Avalon Load (Near Term) | Off-Avalon Load | Avalon -> Off-Avalon | CF -> Lab East | CF->Lab West | CF Load -> MF | CFLCo -> Quebec Market | Labrador Island Link | Maritime Link
Loss Base | -3.94 | -4.94 | 19.06 | -4.3835 | 0 | 0 | -5.8782 | 0.0291 | 0 | 3.19 | 1.4174
Loss Incr | 0.020195 | 0.020195 | 0.020195 | 0.020195 | 0.008209 | -0.0032276 | 0.08174 | -0.0012 | 0 | -0.0076 | 0.019042
Loss Incr2 | 0 | 0 | 0 | 0 | 0.000156 | 0.00029269 | 0 | 5e-05 | 0 | 0.00016 | 0.0002874
| * Loss base 1 MW of HRD station service losses | * Holyrood Modelled as net generation | * Loss base includes 24 MW of HRD station service losses |  |  | *New Losses Based on MF->HVGB Interconnection |  |  | *Sales assumed to be at the border | * Loss Includes 6.9 MW for SOP Converter Station Losses | * Loss includes 0.8 MW for BBK Converter Station Losses
| *Losses updated August 2019 | *Losses updated August 2019 | *Losses updated August 2019 | *Losses updated August 2019 | *Losses updated August 2019 |  |  |  |  | *Losses updated September 2019 | *Losses updated September 2019

## LIL Losses
Bipole
Bipole Mode: | y = 0.00008x2 - 0.0076x - 0.5101 | Per Pole |  |  | Fixed Losses
a | 8e-05 | 0.00016 |  |  | Soldiers Pond Transformer Losses | 0.3
b | -0.0076 | -0.0076 |  |  | Soldiers Pond Synchronous Condenser Losses | 1.6
c | -0.5101 | -0.25505 |  |  | Soldiers Pond Station Service (Synchronous Condensers) | 2
Converter Losses | 6.9 | 3.45 |  |  | Soldiers Pond Station Service | 3
Loss Adjustment | 0 | 0 |  |  | Total | 6.9
c + converter losses |  | 3.195
Flow @ MF | 900 | 450 | 112.5 | 337.5
Line Losses | 57.4499 | 28.725 | 0.91495 | 15.405
Losses | 64.3499 | 32.175 | 4.365 | 18.855
Delivered @ SP | 835.6501 | 417.825 | 108.1351 | 318.645
|  | 835.6501 | 216.2701 | 637.2901
Monopole - Using Bipole Equations
Flow @ MF | 675
Losses | 70.965
Delivered @ SP | 604.035
Monopole - Using Monopole Equations
Monopole Mode: | y = 0.0004664x2 + 0.04x -2.1875
a | 0.0002
b | 0.04
c | -2.1875
Converter Losses | 6.9
Flow @ MF | 675
Losses | 122.8375
Delivered @ SP | 552.1625
Matched
Flow @ MF | 623.2
Losses | 70.965
Delivered @ SP | 552.2351

## Maritime Link Losses
Emera Block Losses
Island Losses |  |  | 70 MW | Emera Block | Half Capacity | Maximum Flow
Loss Eqn | y = 0.0001624x2 + 0.01785x | Emera Block Deliveries | 0 | 158 | 158 | 158
a | 0.0001624 | Additional Flow on ML (MW) | 70 | 0 | 92 | 342
b | 0.017845 | Total Flow on ML | 70 | 158 | 250 | 500
c | 0 | Total Losses | 4.1586 | 11.6006 | 24.1404 | 82.7884
|  | Island Loss | 2.8449 | 7.6737 | 15.4113 | 50.3226
Line Losses |  | Line Loss | 1.3136 | 3.9269 | 8.729 | 32.4657
Loss Eqn | y = 0.000125x2 + 0.011967x + 0.617352 | Delivered | 67.1551 | 150.3263 | 234.5887 | 449.6773
a | 0.000125 | % Island Loss | 68.41% | 66.15% | 63.84% | 60.78% | 63.59%
b | 0.0011967 | % Line Loss | 31.59% | 33.85% | 36.16% | 39.22% | 36.41%
c | 0.61735
BBk Station Service | 0.8
Combined Losses
Loss Eqn | y = 0.000125x2 + 0.011967x + 0.617352
a | 0.0002874
b | 0.019042
c | 1.4174
Split
Island | 64%
Line | 36%

## Island Losses
Island Losses
Total Line Losses
Loss Eqn | y = 0.020195x - 9.32663
x = | Total Customer Load (NF Power + Hydro Rural + Industrial)
a = | 0
b = | 0.020195
c = | -9.3266
Avalon - Off-Avalon Split
Avalon | 53%
Off-Avalon | 47%
Avalon Load Losses
Loss Eqn | y = 0.020195x - 4.94
x = | Total Avalon Load
a = | 0
b = | 0.020195
c = | -4.9431
Off-Avalon Load Losses
Loss Eqn | y = 0.020195x - 4.38
x = | Total Avalon Load
a = | 0
b = | 0.020195
c = | -4.3835

## Lab East New Losses
Lab East 138kV Transmission Line Loss Equation - 33km Section
Load | Losses
0 | 0
13.01 | 0.035
25.95 | 0.131
43.112 | 0.425
63.234 | 0.955
83.402 | 1.738
93.497 | 2.211
103.634 | 2.864