## Capacity
Capacity
| Rated Capacity | Firm Capacity
Unit | MW | MW
Island Generation Capacity
Bay D'Espoir - Unit 1 | 76.5 | 76.5
Bay D'Espoir - Unit 2 | 76.5 | 76.5
Bay D'Espoir - Unit 3 | 76.5 | 76.5
Bay D'Espoir - Unit 4 | 76.5 | 76.5
Bay D'Espoir - Unit 5 | 76.5 | 76.5
Bay D'Espoir - Unit 6 | 76.5 | 76.5
Bay D'Espoir - Unit 7 | 154.4 | 154.4
Cat Arm - Unit 1 | 68.5 | 67
Cat Arm - Unit 2 | 68.5 | 67
Granite Canal | 40 | 40
Hinds Lake | 75 | 75
Paradise River | 8 | 8
Upper Salmon | 84 | 84
Island Hydro Capacity | 957.4 | 954.4
Holyrood Thermal - Unit 1 | 170 | 170
Holyrood Thermal - Unit 2 | 170 | 170
Holyrood Thermal - Unit 3 | 150 | 150
Island Thermal Capacity | 490 | 490
Hardwoods GT | 50 | 50
Hawkes Bay Diesels | 5 | 5
Holyrood Diesels | 12 | 8 | Note 1
Holyrood GT | 123.5 | 123.5
St. Anthony Diesels | 9.7 | 9.7
Stephenville GT | 50 | 50
Island Peaking Capacity | 250.2 | 246.2
Hydro Owned Capacity | 1697.6 | 1690.6
Newfoundland Power - Avalon Hydro | 94.2 | 39.5 | Note 2
Newfoundland Power - Off-Avalon Hydro |  | 20.6 | Note 3
Newfoundland Power - Thermal | 16.5 | 16.5
Newfoundland Power - Greenhill and Wesleyville | 28 | 28
Newfoundland Power Capacity | 138.7 | 104.6
Deer Lake Capacity | 104 | 104
Bishop's Falls - Unit 1-6 | 14.4 | 9.6306
Bishop's Falls - Unit 7 | 2.5 | 1.672
Grand Falls - Beeton | 31 | 20.7325
Grand Falls - Unit 4 | 29.5 | 19.7293
Grand Falls - Unit 5/6 | 8.6 | 5.7516
Grand Falls - Unit 7 | 3.9 | 2.6083
Grand Falls - Unit 8 | 4.3 | 2.8758
Exploits Capacity | 95.6 | 63
Corner Brook CoGen | 15.3 | 8
Fermeuse Wind | 27 | 6 | Note 4
Rattle Brook | 4 | -
St. Lawrence Wind | 27 | 6 | Note 4
Star Lake | 18 | 18
NUG Capacity | 91.3 | 38
Total Island Generation Capacity | 2127.2 | 2000.2
Muskrat Falls Generation Capacity
Muskrat Falls - Unit 1 | 206 | 206
Muskrat Falls - Unit 2 | 206 | 206
Muskrat Falls - Unit 3 | 206 | 206
Muskrat Falls - Unit 4 | 206 | 206
Muskrat Falls Generation Capacity | 824 | 824
Labrador Generation Capacity
Happy Valley CT | 25 | 25
Recall Block | 306.9 | 306.9
TwinCo Block | 225 | 225
Labrador Generation Capacity | 556.9 | 556.9
Capacity Assistance Capacity
CBPP Capacity Assistance | 90 | 90 | Note 5
Vale Diesel Generation | 7.5 | 7.5 | Note 6
MUN Capacity Assistance | 21.7 | 21.7
Vale Interruptible | - | - | Note 7
Newfoundland Power Capacity Assistance | 12 | 12
Island Capacity Assistance Capacity | 131.2 | 131.2
Labrador Capacity Assistance Capacity | 0 | 0
Total Capacity Assistance Capacity | 131.2 | 131.2
Labrador-Island Link ("LIL") Capacity | 642.4 | 642.4 | Note 8,9
Maritime Link ("ML") Capacity | 500 | 158 | Note 10
Island Generation Capacity |  | 2000.2
Island Capacity (Excl. LIL) |  | 2131.4
Island Capacity |  | 2615.8
Labrador Generation Capacity |  | 1380.9
Labrador Capacity |  | 1380.9
1Based on Certificate of Approval AA22-065671, Holyrood Diesels are allowed to operate at 8 MW 06:00-10:00 and 16:00-20:00 from Nov 1 to Apr 30 and 6 MW otherwise.
2Derated to 36 MW for Shortfall Analysis.
3Derated to 18 MW for Shortfall Analysis.
4Based on 2019 ELCC study.
5Derated to 50 MW for Shortfall Analysis.
6Derated to 5.5 MW for Shortfall Analysis.
7Vale Interruptible Load (27 MW) Modeled in the High Load Sensitivity only.
8LIL Capacity modelled at 900 MW as a sensitivity.
9LIL Capacity based on available Labrador capacity less losses and station service
10Based on Emera Block Deliveries adjusted for losses over LTA, LIL and Island Transmission. Capacity measured at Bottom Brook.
Note on A93: Cara Ryan: Removed the reference to the email exchange here - don't want that on record. Please delete this comment in final format.

## Unit Characteristics
Unit Characteristics
| Miniumum Stable Generation | Heat Rate | Fuel Type | Minimum Up Time | Minimum Down Time
Unit |  | GJ/MWh
Island Generation Capacity
Bay D'Espoir - Unit 1 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 2 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 3 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 4 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 5 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 6 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 7 | 0 | - | - | 1 | 1
Cat Arm - Unit 1 | 16 | - | - | 1 | 1
Cat Arm - Unit 2 | 16 | - | - | 1 | 1
Granite Canal | 28 | - | - | 1 | 1
Hinds Lake | 0 | - | - | 1 | 1
Paradise River | 0 | - | - | 1 | 1
Upper Salmon | 0 | - | - | 1 | 1
|  |  |  | 1 | 1
Holyrood Thermal - Unit 1 | 70 | 10.96 -10.32 | #6 Fuel | 1 | 1
Holyrood Thermal - Unit 2 | 70 | 10.96 -10.32 | #6 Fuel | 1 | 1
Holyrood Thermal - Unit 3 | 70 | 10.96 -10.32 | #6 Fuel | 1 | 1
Hardwoods GT | 5 | 19.79 | #2 Diesel - Hardwoods Price | 1 | 1
Hawkes Bay Diesels | 0 | 12.46 | #2 Diesel - Stephenville Price | 1 | 1
Holyrood Diesels | 1 | 12.46 | #2 Diesel - Holyrood Price | 1 | 1
Holyrood GT | 40 | 15.74 | #2 Diesel - Holyrood Price | 4 | 1
St. Anthony Diesels | 0 | 12.46 | #2 Diesel - Stephenville Price | 1 | 1
Stephenville GT | 5 | 21.71 | #2 Diesel - Stephenville Price | 1 | 1
Newfoundland Power - Avalon Hydro | 0 | - | - | 1 | 1
Newfoundland Power - Off-Avalon Hydro | 0 | - | - | 1 | 1
Newfoundland Power - Thermal | 0 | 12.26 | #2 Diesel - Hardwoods Price | 1 | 1
Newfoundland Power - Greenhill and Wesleyville | 0 | 12.26 | #2 Diesel - Hardwoods Price | 1 | 1
Bishop's Falls - Unit 1-6 | 0 | - | - | 1 | 1
Bishop's Falls - Unit 7 | 0 | - | - | 1 | 1
Grand Falls - Beeton | 0 | - | - | 1 | 1
Grand Falls - Unit 4 | 0 | - | - | 1 | 1
Grand Falls - Unit 5/6 | 0 | - | - | 1 | 1
Grand Falls - Unit 7 | 0 | - | - | 1 | 1
Grand Falls - Unit 8 | 0 | - | - | 1 | 1
Corner Brook CoGen | 0 |  | - | 1 | 1
Fermeuse Wind | - | - | - | 1 | 1
Rattle Brook | 0 | - | - | 1 | 1
St. Lawrence Wind | - | - | - | 1 | 1
Star Lake | 0 | - | - | 1 | 1
Muskrat Falls Generation Capacity
Muskrat Falls - Unit 1 | 100 | - | - | 1 | 1
Muskrat Falls - Unit 2 | 100 | - | - | 1 | 1
Muskrat Falls - Unit 3 | 100 | - | - | 1 | 1
Muskrat Falls - Unit 4 | 100 | - | - | 1 | 1
Capacity Assistance Capacity
CBPP Capacity Assistance | - | - | - | 4 | 1
Vale Diesel Generation | - | - | - | 3 | 1
MUN Capacity Assistance | - | - | - | 1 | 1
Vale Interruptible | - | - | - | 1 | 1
Newfoundland Power Capacity Assistance | - | - | - | 3 | 1

## Outage and Maintenance
FOR and Maintenance
Source:
Date:
| Forced Outage Rate | Maintenance Rate
Unit | % | Weeks
Island
Bay D'Espoir - Unit 1 | 3.03 | 3
Bay D'Espoir - Unit 2 | 3.03 | 3
Bay D'Espoir - Unit 3 | 3.03 | 3
Bay D'Espoir - Unit 4 | 3.03 | 3
Bay D'Espoir - Unit 5 | 3.03 | 3
Bay D'Espoir - Unit 6 | 3.03 | 3
Bay D'Espoir - Unit 7 | 3.03 | 3
Cat Arm - Unit 1 | 3.03 | 3
Cat Arm - Unit 2 | 3.03 | 3
Granite Canal | 3.03 | 3
Hinds Lake | 3.03 | 3
Paradise River | 3.03 | 2
Upper Salmon | 3.03 | 3
Holyrood Thermal - Unit 1 | 20 | - | Note 1,2
Holyrood Thermal - Unit 2 | 20 | - | Note 1,2
Holyrood Thermal - Unit 3 | 20 | - | Note 1,2
Newfoundland Power - Avalon Hydro | 5.82 | - | Note 4
Newfoundland Power - Off-Avalon Hydro | 5.82 | - | Note 4
Newfoundland Power - Thermal | 6.19 | - | Note 5
Newfoundland Power - Greenhill and Wesleyville | 30 | -
Hardwoods CT | 30 | 4
Hawkes Bay Diesels | 6.58 | 4 | Note 6
Holyrood CT | 4.9 | 4 | Note 7
Holyrood Diesels | 6.58 | 4 | Note 6
St. Anthony Diesels | 6.58 | 4 | Note 6
Stephenville CT | 30 | 4
Deer Lake - Units | 5.82 | - | Note 4
Bishop's Falls - Unit 1-6 | 3.03 | -
Bishop's Falls - Unit 7 | 3.03 | -
Grand Falls - Beeton | 3.03 | -
Grand Falls - Unit 4 | 3.03 | -
Grand Falls - Unit 5/6 | 3.03 | -
Grand Falls - Unit 7 | 3.03 | -
Grand Falls - Unit 8 | 3.03 | -
Corner Brook CoGen | 19.16 | - | Note 8
Fermuse Wind | - | - | Note 9
Rattle Brook | 5.82 | - | Note 4
St. Lawrence Wind | - | - | Note 9
Star Lake | 3.03 | 3
Muskrat Falls
Muskrat Falls - Unit 1 | 3.03 | 3
Muskrat Falls - Unit 2 | 3.03 | 3
Muskrat Falls - Unit 3 | 3.03 | 3
Muskrat Falls - Unit 4 | 3.03 | 3
Labrador
Happy Valley CT | 4.65 | 4
Recall Block | - | - | Note 10
TwinCo Block | - | - | Note 10
Transmission
Labrador-Island Link A | 0 | -
Labrador-Island Link B | 0 | -
Labrador-Island Link Bipole | 5 | - | Note 11
1Maintenance assumed to be completed during total plant outage in summer
220% FOR for Holyrood TGS is the base case and is based on historical outage data
4Based on 2021 G-ERIS, Table 6.1.2, DAFOR, All Units
5Based on 2021 G-ERIS, Table 6.3.2, DAUFOP, All Units
6Generating Unit Statistical Brochure 4 2017-2021, EFORd, Diesel, All Sizes
7Based on a scenario approach
8Based on 2021 G-ERIS, Table 6.2.18, DAUFOP, All Units
9Forced outage rate and maintenance included in probability distribution
10Assumed to be always available
11Sensitivities modelled for 0%, 1%, 10% and 100%
12Maintenance is not modelled for units not owned by Hydro (Newfoundland Power, Deer Lake, Exploits, Corner Brook CoGen and Rattle Brook)

## #2 Fuel Price
Annual Fuel Oil No 2 Price
| Holyrood CT1 | Hardwoods GT2 | Stephenville GT2 | Happy Valley GT2 |  | Holyrood CT | Hardwoods GT | Stephenville GT | Happy Valley GT
Year | $CDN/L | $CDN/L | $CDN/L | $CDN/L |  | $/GJ | $/GJ | $/GJ | $/GJ | Gas Tubine #2 Heat Content | 5.825 | MBtu/bbl
2025 | 1.03 | 1.2767 | 1.3067 | 1.565 | 2025 | 26.6452 | 33.028 | 33.8041 | 40.4852 | Barrels -> Liters | 158.987 | L/bbl
2026 | 1.05 | 1.337 | 1.367 | 1.625 | 2026 | 27.1626 | 34.5861 | 35.3622 | 42.0374 | Mbtu -> GJ | 0.9478 | Mbtu/GJ
2027 | 1.06 | 1.3872 | 1.4172 | 1.675 | 2027 | 27.4213 | 35.8855 | 36.6616 | 43.3308
2028 | 1.135 | 1.5024 | 1.5324 | 1.715 | 2028 | 29.3615 | 38.8664 | 39.6425 | 44.3656
2029 | 1.135 | 1.5427 | 1.5727 | 1.755 | 2029 | 29.3615 | 39.9071 | 40.6832 | 45.4004
2030 | 1.14 | 1.5879 | 1.6179 | 1.805 | 2030 | 29.4908 | 41.0772 | 41.8533 | 46.6938
2031 | 1.155 | 1.6129 | 1.6429 | 1.83 | 2031 | 29.8789 | 41.7254 | 42.5015 | 47.3406
2032 | 1.175 | 1.6329 | 1.6629 | 1.85 | 2032 | 30.3963 | 42.2428 | 43.0189 | 47.858
2033 | 1.19 | 1.6479 | 1.6779 | 1.87 | 2033 | 30.7843 | 42.6308 | 43.4069 | 48.3753
2034 | 1.205 | 1.6629 | 1.6929 | 1.885 | 2034 | 31.1723 | 43.0189 | 43.7949 | 48.7634
1The Holyrood Combustion Turbine ("CT") is regulated by the Management of Greenhouse Gas Act and is exempted from the provincial carbon tax until July 1, 2023.
This facility will remain exempted from the federal fuel charge (federal carbon tax) after July 1, 2023, assuming Hydro completes the necessary regulatory process.
2The remaining on-grid peaking stations are gas turbines ("GT") at Hardwoods, Stephenville and Happy Valley, which are exempted from the provincial carbon tax until July 1, 2023. They will be
subject to the federal fuel charge after July 1, 2023.

## #6 Fuel Price
Annual Fuel Oil No 6 Price
| Holyrood Thermal #61 |  | Holyrood Thermal #6
| $CDN/BBL |  | $/GJ | Holyrood #6 Heat Content | 6.287 | MBtu/bbl
2025 | 104.7 | 2025 | 15.7841 | Mbtu -> GJ | 0.9478 | Mbtu/GJ
2026 | 100.4 | 2026 | 15.1359
2027 | 95.8 | 2027 | 14.4424
2028 | 95.5 | 2028 | 14.3972
2029 | 94.7 | 2029 | 14.2765
2030 | 93.2 | 2030 | 14.0504
2031 | 93.6 | 2031 | 14.1107
2032 | 94.9 | 2032 | 14.3067
2033 | 96.5 | 2033 | 14.5479
2034 | 98 | 2034 | 14.774
1The Holyrood Thermal Generating Station is regulated by the Management of Greenhouse Gas Act. This facility is exempted from the provincial carbon tax until July 1, 2023.
This facility will remain exempted from the federal fuel charge (federal carbon tax) after July 1, 2023, assuming Hydro completes the necessary regulatory process.

## Loss Equations
Loss Equations
Line | Constant | Linear | Quadratic
Avalon Load (Long Term) | -3.94 | 0.020195 | 0 | Note 1
Avalon Load (Near Term Production) | -4.94 | 0.020195 | 0 | Note 2
Avalon Load (Near Term Reliability) | 19.06 | 0.020195 | 0 | Note 3
Off-Avalon Load | -4.3835 | 0.020195 | 0
Avalon -> Off-Avalon | 0 | 0.008209 | 0.000156
MF -> Lab East | -0.0776 | 0.0067 | 0.0002 | Note 4
CF -> Lab West | -5.8782 | 0.08174 | 0
CF Load -> MF | 0.0291 | -0.0012 | 5e-05
CFLCo -> Quebec Market | 0 | 0 | 0
Labrador Island Link (Per Pole) | 6.545 | 0.0076 | 0.00016 | Note 5,6
Labrador Island Link (Both Poles) | 13.0899 | 0.0076 | 8e-05 | Note 5,7
Maritime Link | 1.417 | 0.02981 | 0.0002874 | Note 8,9
1Includes 1 MW of Holyrood station service losses
2For production plan Holyrood is modelled as net generation
3Includes 24 MW of Holyrood station service losses
4Updated to include MF - HVGB interconnection
5Includes 13.6 MW of SOP converter station losses
6Per Pole Loss Equation is used in the Reliability Model
7Both Pole Loss Equation is used in the Production/Expansion Model
8Includes 0.8 MW of Bottom Brook converter station losses
9Combined Equation for Line and Island Losses

## Expansion Options
Expansion Options
Batteries
Plant Name | Capacity | Firm Capacity | Min Stable Generation | Heat Rate | Fuel Type | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Rate | Capital Cost1,2 | Fixed O&M1 | Variable O&M1 | Asset Life3 | Round Trip Efficiency | Duration
| MW | MW | MW | GJ/MWh |  | hrs | hrs | % | Weeks | $/kW | $/kW/year | $/MWh | years | % | hrs
GE LM6000 Combustion Turbine ("CT") | 141.6 | 141.6 | 35.4 | 9.167 | #2 Diesel - Hardwoods Price | 1 | 1 | 4.9 | 4 | 3204.4653 | 20 | 6 | 35 | - | -
Portland Creek | 23 | 23 | 2.3 | - | - | 1 | 1 | 3.03 | 3 | 15746.3896 | 119.1555 | 7.8848 | 60 | - | -
Island Pond | 36 | 36 | 7.2 | - | - | 1 | 1 | 3.03 | 3 | 15569.8159 | 121.006 | 7.8848 | 60 | - | -
Round Pond | 18 | 18 | 3.6 | - | - | 1 | 1 | 3.03 | 3 | 19055.4105 | 143.5165 | 7.8848 | 60 | - | -
BDE Unit 8 | 154.4 | 154.4 | - | - | - | 1 | 1 | 3.03 | 3 | 3345.0425 | 16.1575 | 7.8848 | 60 | - | -
Cat Arm Unit 3 | 68.2 | 68.2 | 16 | - | - | 1 | 1 | 3.03 | 3 | 4661.8616 | 24.2969 | 7.8848 | 60 | - | -
Wind 100 MW | 100 | 22 | - | - | - | 1 | 1 | - | 1 | 2082.0083 | 48 | 0 | 20 | - | -
Solar | 20 | 0 | - | - | - | 1 | 1 | 0.5 | 1 | 1659.0204 | 26.1 | 0 | 25 | - | -
Battery | 50 | 30 | - | - | - | 1 | 1 | 0.5 | 0 | 2220.8831 | 88.8353 | 0 | 20 | 85% | 4
Proxy Capacity | 50 | 50 | 10 | 10.968 | #2 Diesel - Holyrood Price | 1 | 1 | 4.9 | 4 | 10000 | 20 | 6 | 35 | - | -
1All costs are in 2023 dollars
2Based on Rated Capacity.
3CT and Hydro asset life based on the 2012 Depreciation Methodology Application. Wind asset life based on the service life of existing wind farms @ Fermeuse & Stephenville. Battery asset life based on BESS estimate from Wood (Page 2 of Attachment 1 of BESS Study filed September 29, 2023). Solar asset life based on NREL low lifespan estimate.