## Scenario 1AEF
Year | New Generation (MW) |  |  |  |  | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Wind
2031 | 141.6 | 0 | 22 | 222.6 | 66 | 1967 | 1014 | 1666 | 680 | 857 | 157 | 144 | 239 | 84.52% | 92.02% | 1807 | 779 | 932 | 82 | 78 | 98 | 91.91% | 95.83% | 1905 | 850 | 982 | 32 | 30 | 96.84% | 96.85%
2034 | 141.6 | 50 | 27.5 | 222.6 | 82.5 | 2051 | 1062 | 1762 | 691 | 912 | 150 | 139 | 216 | 85.88% | 92.69% | 1880 | 774 | 974 | 88 | 83 | 98 | 91.71% | 95.71% | 1978 | 841 | 1025 | 37 | 36 | 96.52% | 96.44%
*Includes Transmission Losses and Station Service Loads. After Curtailment
Supplied from PSSE
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation
-SVL and existing wind retired
-HRD Thermal retired (HRD U3 as SC)
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 1A (hidden)
Year | New Generation (MW) |  |  |  |  | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Wind
2031 | 283.2 | 0 | 22 | 154.4 | 66 | 1928 | 1010 | 1858 | 683 | 972 | 38 | 32 | 0 | 96.24% | 96.37% | No Violation |  |  | 0 | 0 | 0 | 100% | 100% | Generation Does Not Max Out |  |  | 0 | 0 | 100% | 100%
2034 | 283.2 | 0 | 27.5 | 154.4 | 82.5 | 2022 | 1058 | 1866 | 683 | 977 | 81 | 75 | 131 | 92.34% | 95.99% | 1997 | 774 | 1046 | 12 | 13 | 0 | 98.87% | 98.76% | 1997 | 774 | 1046 | 12 | 13 | 98.87% | 98.76%
2038 | 424.8 | 0 | 38.5 | 154.4 | 115.5 | 2162 | 1143 | 2079 | 680 | 1099 | 44 | 39 | 0 | 96.15% | 96.16% | 2150 | 728 | 1137 | 6 | 6 | 0 | 99.48% | 99.44% | Generation Does Not Max Out |  |  | 0 | 0 | 100% | 100%
*Includes Transmission Losses and Station Service Loads. After Curtailment | [23 empty] | No improvement with Reactive Power Support added in 2034, because you max out of generation the same time. Therefore reactive power support can't be justified unless additional generation added
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation
-SVL and existing wind retired
-HRD Thermal retired (HRD U3 as SC)
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 1AEI
Year | New Generation (MW) | [5 empty] | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Thermal | Wind
2031 | 141.6 | 0 | 22 | 154.4 | 75 | 66 | 1963 | 1014 | 1665 | 686 | 862 | 152 | 146 | 247 | 85.01% | 92.26% | 1808 | 780 | 935 | 79 | 76 | 104 | 92.21% | 95.98% | 1912 | 855 | 989 | 25 | 26 | 97.53% | 97.4%
2034 | 141.6 | 0 | 27.5 | 222.6 | 75 | 82.5 | 2070 | 1064 | 1678 | 675 | 861 | 203 | 189 | 325 | 80.92% | 90.19% | 1817 | 773 | 935 | 129 | 124 | 186 | 87.88% | 93.77% | 2003 | 908 | 1031 | 33 | 34 | 96.9% | 96.76%
*Includes Transmission Losses and Station Service Loads. After Curtailment
Supplied from PSSE
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation
-SVL and existing wind retired
-HRD Thermal retired (HRD U3 as SC)
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 2 (hidden)
Year | New Generation (MW) |  |  |  |  | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Wind
2031 | 141.6 | 50 | 27.5 | 222.6 | 82.5 | 2056 | 1065 | 1753 | 685 | 907 | 158 | 145 | 221 | 85.16% | 92.32% | 1883 | 775 | 975 | 90 | 83 | 91 | 91.55% | 95.62% | 1974 | 841 | 1023 | 42 | 40 | 96.06% | 96.01%
2034 | 141.6 | 150 | 38.5 | 222.6 | 115.5 | 2187 | 1141 | 1906 | 681 | 995 | 146 | 135 | 216 | 87.2% | 93.32% | 2018 | 758 | 1054 | 87 | 82 | 104 | 92.38% | 96.02% | 2122 | 829 | 1108 | 33 | 32 | 97.11% | 97.03%
2038 | 141.6 | 400 | 55 | 222.6 | 165 | 2415 | 1284 | 2289 | 683 | 1219 | 65 | 61 | 0 | 94.94% | 94.78% | 2384 | 731 | 1253 | 31 | 0 | 0 | 97.59% | 98.72% | Generation Does Not Max Out |  |  | 0 | 0 | 100% | 100%
*Includes Transmission Losses and Station Service Loads. After Curtailment
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation | [7 empty] | Year 2038
-SVL and existing wind retired | [7 empty] | Voltage issues appear on NP system within SSD/STB loop
-HRD Thermal retired (HRD U3 as SC) | [7 empty] | *Likely a common issue at that growth level.
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 2A (hidden)
Year | New Generation (MW) |  |  |  |  | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [8 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Wind
2031 | 283.2 | 0 | 27.5 | 154.4 | 82.5 | 2028 | 1062 | 1868 | 683 | 978 | 84 | 76 | 130 | 92.09% | 95.86% | Generation Maxed Out |  |  | 16 | 14 |  |  | 98.49% | 98.52% | 1998 | 772 | 1046 | 16 | 14 | 98.49% | 98.52%
2034 | 283.2 | 0 | 38.5 | 222.6 | 115.5 | 2189 | 1141 | 1925 | 683 | 989 | 152 | 112 | 188 | 86.68% | 93.06% | 1990 | 764 | 1052 | 89 | 0 | 110 | 123 | 92.2% | 95.93% | 2113 | 835 | 1102 | 39 | 37 | 96.58% | 96.53%
2038 | 566.4 | 0 | 55 | 222.6 | 165 | 2383 | 1277 | No Violation |  |  | 0 | #VALUE! | 0 | 100% | 100% | No Violation |  |  | 0 | 0 |  |  | 100% | 100% | Generation Does Not Max Out |  |  | 0 | 0 | 100% | 100%
*Includes Transmission Losses and Station Service Loads. After Curtailment
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation | [7 empty] | Year 2038
-SVL and existing wind retired | [7 empty] | Voltage issues appear on NP system within SSD/STB loop
-HRD Thermal retired (HRD U3 as SC) | [7 empty] | *Likely a common issue at that growth level.
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 4AEF
Year | New Generation (MW) |  |  |  |  | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Wind
2031 | 0 | 0 | 22 | 154.4 | 66 | 1948 | 996 | 1395 | 635 | 707 | 289 | 264 | 314 | 70.98% | 85.16% | 1601 | 779.5 | 819 | 177 | 170 | 108 | 82.23% | 87.73% | 1709 | 856 | 875 | 121 | 118 | 87.85% | 87.73%
2034 | 141.6 | 0 | 22 | 154.4 | 66 | 1971 | 1023 | 1667 | 686 | 863 | 160 | 144 | 187 | 84.36% | 91.88% | 1800 | 779.01 | 934 | 89 | 82 | 54 | 91.3% | 94.06% | 1854 | 817 | 963 | 60 | 57 | 94.13% | 94.06%
*Includes Transmission Losses and Station Service Loads. After Curtailment
Supplied from PSSE
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation
-SVL and existing wind retired
-HRD Thermal retired (HRD U3 as SC)
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 4AEF(ADV)
Year | New Generation (MW) |  |  |  |  | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Wind
2031 | 141.6 | 0 | 22 | 154.4 | 66 | 1902 | 987 | 1668 | 686 | 864 | 123 | 111 | 184 | 87.54% | 93.53% | 1804 | 780 | 935 | 52 | 46 | 48 | 94.73% | 97.27% | 1852 | 815 | 961 | 26 | 24 | 97.37% | 97.37%
2034 | 141.6 | 0 | 22 | 154.4 | 66 | 1971 | 1023 | 1667 | 686 | 863 | 160 | 144 | 187 | 84.36% | 91.88% | 1800 | 779.01 | 934 | 89 | 54 | 54 | 91.3% | 94.06% | 1854 | 817 | 963 | 60 | 57 | 94.13% | 94.06%
*Includes Transmission Losses and Station Service Loads. After Curtailment
Supplied from PSSE
Assumptions:
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation
-SVL and existing wind retired
-HRD Thermal retired (HRD U3 as SC)
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)

## Scenario 4AEI
Year | New Generation (MW) | [5 empty] | Peak Conditions (LIL Outage) (MW) |  | 1st Thermal Violation (No Upgrade) | [7 empty] | Voltage Violation (Option 4 Applied) | [7 empty] | Island Generation Maxed Out (Option 4 + Cap Bank (SSD) + STATCOM - $350M-$400M)
| On-Avalon |  |  | Off-Avalon |  |  | Island Load* | Gross Avalon Load | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) |  |  | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served | Island Load (MW)* | BDE Flow (East) (MW) | Gross Avalon Load (MW) | Avalon Load Shed (MW) | Off Avalon Load Shed (MW) | Percent of Peak Gross Avalon Demand Served | Percent of Peak Island Demand Served
| CT | Proxy Capacity Resource | Wind | Hydro | Thermal | Wind
2031 | 0 | 0 | 22 | 154.4 | 75 | 66 | 1951 | 996 | 1399 | 633 | 707 | 289 | 263 | 387 | 70.98% | 85.19% | 1652 | 808 | 844 | 152 | 147 | 134 | 84.74% | 91.54% | 1786 | 907 | 914 | 82 | 83 | 91.77% | 91.54%
2034 | 0 | 0 | 22 | 154.4 | 75 | 66 | 2031 | 1034 | 1399 | 633 | 708 | 326 | 306 | 387 | 68.47% | 83.95% | 1652 | 808 | 844 | 190 | 189 | 134 | 81.62% | 87.94% | 1786 | 907 | 914 | 120 | 125 | 88.39% | 87.94%
-Given reactive power support is required without even considering 230kV contingnencies
*Includes Transmission Losses and Station Service Loads. After Curtailment | [16 empty] | we assume it would be the same as Cap Bank (SSD) + STATCOM ($200M-$250M)
Further analysis would be required to optimize. Any SPS could potentially help, but it would
Assumptions: | [16 empty] | likely require GE support, because it would a trigger on LIL bipole trip.
-All new Avalon Generation connected electrically downstream of TL201/TL217
-Proporational spread of load growth | [5 empty] | Supplied from PSSE
-HRD CT online at 123.5 MW
-39 MW of NL Avalon Generation
-SVL and existing wind retired
-HRD Thermal retired (HRD U3 as SC)
-No new generation provided much reactive power support (capability curves N/A)
-2 SOPSCs online
-LIL Bipole Outage. ML as STATCOM (0 MW Output)