## Capacity
Capacity
| Rated Capacity | Firm Capacity
Unit | MW | MW
Island Generation Capacity
Bay D'Espoir - Unit 1 | 76.5 | 76.5
Bay D'Espoir - Unit 2 | 76.5 | 76.5
Bay D'Espoir - Unit 3 | 76.5 | 76.5
Bay D'Espoir - Unit 4 | 76.5 | 76.5
Bay D'Espoir - Unit 5 | 76.5 | 76.5
Bay D'Espoir - Unit 6 | 76.5 | 76.5
Bay D'Espoir - Unit 7 | 154.4 | 154.4
Cat Arm - Unit 1 | 68.5 | 67
Cat Arm - Unit 2 | 68.5 | 67
Granite Canal | 40 | 40
Hinds Lake | 75 | 75
Paradise River | 8 | 8
Upper Salmon | 84 | 84
Island Hydro Capacity | 957.4 | 954.4
Holyrood Thermal - Unit 1 | 170 | 170
Holyrood Thermal - Unit 2 | 170 | 170
Holyrood Thermal - Unit 3 | 150 | 150
Island Thermal Capacity | 490 | 490
Hardwoods GT | 50 | 50
Hawkes Bay Diesels | 5 | 5
Holyrood Diesels | 12 | 8 | Note 1
Holyrood GT | 123.5 | 123.5
St. Anthony Diesels | 9.7 | 9.7
Stephenville GT | 50 | 50
Island Peaking Capacity | 250.2 | 246.2
Hydro Owned Capacity | 1697.6 | 1690.6
Newfoundland Power - Avalon Hydro | 78.6 | 39.5 | Note 2
Newfoundland Power - Off-Avalon Hydro |  | 20.6 | Note 3
Newfoundland Power - Thermal | 16.5 | 16.5
Newfoundland Power - Greenhill and Wesleyville | 28 | 28
Newfoundland Power Capacity | 123.1 | 104.6
Deer Lake Capacity | 104 | 104
Bishop's Falls - Unit 1-6 | 18 | 9.6306
Bishop's Falls - Unit 7 | 2.2 | 1.672
Grand Falls - Beeton | 30 | 20.7325
Grand Falls - Unit 4 | 27.6 | 19.7293
Grand Falls - Unit 5/6 | 8 | 5.7516
Grand Falls - Unit 7 | 4 | 2.6083
Grand Falls - Unit 8 | 4 | 2.8758
Exploits Capacity | 95.6 | 63
Corner Brook CoGen | 15.3 | 8
Fermeuse Wind | 27 | 6 | Note 4
Rattle Brook | 4 | -
St. Lawrence Wind | 27 | 6 | Note 4
Star Lake | 18 | 18
NUG Capacity | 91.3 | 38
Total Island Generation Capacity | 2111.6 | 2000.2
Muskrat Falls Generation Capacity
Muskrat Falls - Unit 1 | 206 | 206
Muskrat Falls - Unit 2 | 206 | 206
Muskrat Falls - Unit 3 | 206 | 206
Muskrat Falls - Unit 4 | 206 | 206
Muskrat Falls Generation Capacity | 824 | 824
Labrador Generation Capacity
Happy Valley CT | 25 | 25
Recall Block | 306.9 | 306.9
TwinCo Block | 225 | 225
Labrador Generation Capacity | 556.9 | 556.9
Capacity Assistance Capacity
CBPP Capacity Assistance | 90 | 90 | Note 5
Vale Diesel Generation | 7.5 | 7.5 | Note 6
MUN Capacity Assistance | 21.7 | 21.7
Vale Interruptible | - | - | Note 7
Newfoundland Power Capacity Assistance | 12 | 12
Island Capacity Assistance Capacity | 131.2 | 131.2
Labrador Capacity Assistance Capacity | 0 | 0
Total Capacity Assistance Capacity | 131.2 | 131.2
Labrador-Island Link ("LIL") Capacity | 642.4 | 642.4 | Note 8,9
Maritime Link ("ML") Capacity | 500 | 158 | Note 10
Island Generation Capacity |  | 2000.2
Island Capacity (Excl. LIL) |  | 2131.4
Island Capacity |  | 2615.8
Labrador Generation Capacity |  | 1380.9
Labrador Capacity |  | 1380.9
1Based on Certificate of Approval AA22-065671, Holyrood Diesels are allowed to operate at 8 MW 06:00-10:00 and 16:00-20:00 from Nov 1 to Apr 30 and 6 MW otherwise.
2Derated to 36 MW for Shortfall Analysis.
3Derated to 18 MW for Shortfall Analysis.
4Based on 2019 ELCC study.
5Derated to 50 MW for Shortfall Analysis.
6Derated to 5.5 MW for Shortfall Analysis.
7Vale Interruptible Load (27 MW) Modeled in the High Load Sensitivity only.
8LIL Capacity modelled at 900 MW as a sensitivity.
9LIL Capacity based on available Labrador capacity less losses and station service
10Based on Emera Block Deliveries adjusted for losses over LTA, LIL and Island Transmission. Capacity measured at Bottom Brook.

## Unit Characteristics
Unit Characteristics
| Miniumum Stable Generation | Heat Rate | Fuel Type | Minimum Up Time | Minimum Down Time
Unit |  | GJ/MWh
Island Generation Capacity
Bay D'Espoir - Unit 1 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 2 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 3 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 4 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 5 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 6 | 0 | - | - | 1 | 1
Bay D'Espoir - Unit 7 | 0 | - | - | 1 | 1
Cat Arm - Unit 1 | 16 | - | - | 1 | 1
Cat Arm - Unit 2 | 16 | - | - | 1 | 1
Granite Canal | 28 | - | - | 1 | 1
Hinds Lake | 0 | - | - | 1 | 1
Paradise River | 0 | - | - | 1 | 1
Upper Salmon | 0 | - | - | 1 | 1
Holyrood Thermal - Unit 1 | 70 | 10.96 -10.32 | #6 Fuel | 1 | 1
Holyrood Thermal - Unit 2 | 70 | 10.96 -10.32 | #6 Fuel | 1 | 1
Holyrood Thermal - Unit 3 | 70 | 10.96 -10.32 | #6 Fuel | 1 | 1
Hardwoods GT | 5 | 19.79 | #2 Diesel - Hardwoods Price | 1 | 1
Hawkes Bay Diesels | 0 | 12.46 | #2 Diesel - Stephenville Price | 1 | 1
Holyrood Diesels | 1 | 12.46 | #2 Diesel - Holyrood Price | 1 | 1
Holyrood GT | 40 | 15.74 | #2 Diesel - Holyrood Price | 4 | 1
St. Anthony Diesels | 0 | 12.46 | #2 Diesel - Stephenville Price | 1 | 1
Stephenville GT | 5 | 21.71 | #2 Diesel - Stephenville Price | 1 | 1
Newfoundland Power - Avalon Hydro | 0 | - | - | 1 | 1
Newfoundland Power - Off-Avalon Hydro | 0 | - | - | 1 | 1
Newfoundland Power - Thermal | 0 | 12.26 | #2 Diesel - Hardwoods Price | 1 | 1
Newfoundland Power - Greenhill and Wesleyville | 0 | 12.26 | #2 Diesel - Hardwoods Price | 1 | 1
Bishop's Falls - Unit 1-6 | 0 | - | - | 1 | 1
Bishop's Falls - Unit 7 | 0 | - | - | 1 | 1
Grand Falls - Beeton | 0 | - | - | 1 | 1
Grand Falls - Unit 4 | 0 | - | - | 1 | 1
Grand Falls - Unit 5/6 | 0 | - | - | 1 | 1
Grand Falls - Unit 7 | 0 | - | - | 1 | 1
Grand Falls - Unit 8 | 0 | - | - | 1 | 1
Corner Brook CoGen | 0 |  | - | 1 | 1
Fermeuse Wind | - | - | - | 1 | 1
Rattle Brook | 0 | - | - | 1 | 1
St. Lawrence Wind | - | - | - | 1 | 1
Star Lake | 0 | - | - | 1 | 1
Muskrat Falls Generation Capacity
Muskrat Falls - Unit 1 | 100 | - | - | 1 | 1
Muskrat Falls - Unit 2 | 100 | - | - | 1 | 1
Muskrat Falls - Unit 3 | 100 | - | - | 1 | 1
Muskrat Falls - Unit 4 | 100 | - | - | 1 | 1
Capacity Assistance Capacity
CBPP Capacity Assistance | - | - | - | 4 | 1
Vale Diesel Generation | - | - | - | 3 | 1
MUN Capacity Assistance | - | - | - | 1 | 1
Vale Interruptible | - | - | - | 1 | 1
Newfoundland Power Capacity Assistance | - | - | - | 3 | 1

## Outage and Maintenance
FOR and Maintenance
Source:
Date:
| Forced Outage Rate | Maintenance Rate | Availability Factor
Unit | % | Weeks | %
Island
Bay D'Espoir - Unit 1 | 3.03 | 3 | 91.2%
Bay D'Espoir - Unit 2 | 3.03 | 3 | 91.2%
Bay D'Espoir - Unit 3 | 3.03 | 3 | 91.2%
Bay D'Espoir - Unit 4 | 3.03 | 3 | 91.2%
Bay D'Espoir - Unit 5 | 3.03 | 3 | 91.2%
Bay D'Espoir - Unit 6 | 3.03 | 3 | 91.2%
Bay D'Espoir - Unit 7 | 3.03 | 3 | 91.2%
Cat Arm - Unit 1 | 3.03 | 3 | 91.2%
Cat Arm - Unit 2 | 3.03 | 3 | 91.2%
Granite Canal | 3.03 | 3 | 91.2%
Hinds Lake | 3.03 | 3 | 91.2%
Paradise River | 3.03 | 2 | 93.12%
Upper Salmon | 3.03 | 3 | 91.2%
Holyrood Thermal - Unit 1 | 20 | 0 | 80% | Note 1,2
Holyrood Thermal - Unit 2 | 20 | 0 | 80% | Note 1,2
Holyrood Thermal - Unit 3 | 20 | 0 | 80% | Note 1,2
Newfoundland Power - Avalon Hydro | 5.82 | 0 | 94.18% | Note 4
Newfoundland Power - Off-Avalon Hydro | 5.82 | 0 | 94.18% | Note 4
Newfoundland Power - Thermal | 6.19 | 0 | 93.81% | Note 5
Newfoundland Power - Greenhill and Wesleyville | 30 | 0 | 70%
Hardwoods CT | 30 | 0 | 62.31%
Hawkes Bay Diesels | 6.58 | 4 | 85.73% | Note 6
Holyrood CT | 4.9 | 4 | 87.41% | Note 7
Holyrood Diesels | 6.58 | 4 | 85.73% | Note 6
St. Anthony Diesels | 6.58 | 4 | 85.73% | Note 6
Stephenville CT | 30 | 0 | 62.31%
Deer Lake - Units | 5.82 | 0 | 94.18% | Note 4
Bishop's Falls - Unit 1-6 | 3.03 | 0 | 96.97%
Bishop's Falls - Unit 7 | 3.03 | 0 | 96.97%
Grand Falls - Beeton | 3.03 | 0 | 96.97%
Grand Falls - Unit 4 | 3.03 | 0 | 96.97%
Grand Falls - Unit 5/6 | 3.03 | 0 | 96.97%
Grand Falls - Unit 7 | 3.03 | 0 | 96.97%
Grand Falls - Unit 8 | 3.03 | 0 | 96.97%
Corner Brook CoGen | 19.16 | 0 | 80.84% | Note 8
Fermuse Wind | 0 | 0 | 100% | Note 9
Rattle Brook | 5.82 | 0 | 94.18% | Note 4
St. Lawrence Wind | 0 | 0 | 100% | Note 9
Star Lake | 3.03 | 2 | 93.12%
Muskrat Falls
Muskrat Falls - Unit 1 | 3.03 | 3 | 91.2%
Muskrat Falls - Unit 2 | 3.03 | 3 | 91.2%
Muskrat Falls - Unit 3 | 3.03 | 3 | 91.2%
Muskrat Falls - Unit 4 | 3.03 | 3 | 91.2%
Labrador
Happy Valley CT | 4.65 | 4 | 87.66%
Recall Block | 0 | 0 | 100% | Note 10
TwinCo Block | 0 | 0 | 100% | Note 10
Transmission
Labrador-Island Link A | 0 | 1.5 | 97.12%
Labrador-Island Link B | 0 | 1.5 | 97.12%
Labrador-Island Link Bipole | 1 | 1 | 97.08% | Note 11
1Maintenance assumed to be completed during total plant outage in summer
220% FOR for Holyrood TGS is the base case and is based on historical outage data
4Based on 2021 G-ERIS, Table 6.1.2, DAFOR, All Units
5Based on 2021 G-ERIS, Table 6.3.2, DAUFOP, All Units
6Generating Unit Statistical Brochure 4 2017-2021, EFORd, Diesel, All Sizes
7Based on a scenario approach
8Based on 2021 G-ERIS, Table 6.2.18, DAUFOP, All Units
9Forced outage rate and maintenance included in probability distribution
10Assumed to be always available
11Sensitivities modelled for 5%
12Maintenance is not modelled for units not owned by Hydro (Newfoundland Power, Deer Lake, Exploits, Corner Brook CoGen and Rattle Brook)

## #2 Fuel Price
Annual Fuel Oil No 2 Price | [9 empty] | Gas Tubine #2 Heat Content | 5.825 | MBtu/bbl
[10 empty] | Barrels -> Liters | 158.987 | L/bbl
| Holyrood CT | Hardwoods GT | Stephenville GT | Happy Valley GT |  | Holyrood CT | Hardwoods GT | Stephenville GT | Happy Valley GT | Mbtu -> GJ | 0.9478 | Mbtu/GJ
Year | $CDN/L | $CDN/L | $CDN/L | $CDN/L |  | $/GJ | $/GJ | $/GJ | $/GJ
2026 | 1.0408 | 1.0448 | 1.1028 | 0.78625 | 2026 | 26.9255 | 27.029 | 28.5294 | 20.3396
2027 | 1.0012 | 1.0052 | 1.0633 | 0.74125 | 2027 | 25.9015 | 26.005 | 27.5054 | 19.1755
2028 | 1.085 | 1.089 | 1.147 | 0.835 | 2028 | 28.068 | 28.1715 | 29.6719 | 21.6008
2029 | 1.14 | 1.144 | 1.202 | 0.895 | 2029 | 29.4908 | 29.5943 | 31.0947 | 23.1529
2030 | 1.205 | 1.209 | 1.267 | 0.965 | 2030 | 31.1723 | 31.2758 | 32.7762 | 24.9637
2031 | 1.285 | 1.289 | 1.347 | 1.045 | 2031 | 33.2419 | 33.3454 | 34.8458 | 27.0333
2032 | 1.33 | 1.334 | 1.392 | 1.095 | 2032 | 34.406 | 34.5095 | 36.0099 | 28.3267
2033 | 1.38 | 1.384 | 1.442 | 1.15 | 2033 | 35.6994 | 35.8029 | 37.3033 | 29.7495
2034 | 1.43 | 1.434 | 1.492 | 1.205 | 2034 | 36.9929 | 37.0964 | 38.5968 | 31.1723
2035 | 1.46 | 1.464 | 1.522 | 1.24 | 2035 | 37.769 | 37.8725 | 39.3729 | 32.0778

## #6 Fuel Price
Annual Fuel Oil No 6 Price |  |  |  | Holyrood #6 Heat Content | 6.287 | MBtu/bbl
|  |  |  | Mbtu -> GJ | 0.9478 | Mbtu/GJ
| Holyrood Thermal #6 |  | Holyrood Thermal #6
| $CDN/BBL |  | $/GJ
2026 | 80.3833 | 2026 | 12.1182
2027 | 78.8 | 2027 | 11.8795
2028 | 84.4 | 2028 | 12.7238
2029 | 88.4 | 2029 | 13.3268
2030 | 93.7 | 2030 | 14.1258
2031 | 100.1 | 2031 | 15.0906
2032 | 104.1 | 2032 | 15.6937
2033 | 108.1 | 2033 | 16.2967
2034 | 112.1 | 2034 | 16.8997
2035 | 113.2 | 2035 | 17.0655

## Loss Equations
Loss Equations
Line | Constant | Linear | Quadratic
Avalon Load (Long Term) | -3.94 | 0.020195 | 0 | Note 1
Avalon Load (Near Term Production) | -4.94 | 0.020195 | 0 | Note 2
Avalon Load (Near Term Reliability) | 19.06 | 0.020195 | 0 | Note 3
Off-Avalon Load | -4.3835 | 0.020195 | 0
Avalon -> Off-Avalon | 0 | 0.008209 | 0.000156
MF -> Lab East | -0.0776 | 0.0067 | 0.0002 | Note 4
CF -> Lab West | -5.8782 | 0.08174 | 0
CF Load -> MF | 0.0291 | -0.0012 | 5e-05
CFLCo -> Quebec Market | 0 | 0 | 0
Labrador Island Link (Per Pole) | 6.545 | 0.0076 | 0.00016 | Note 5,6
Labrador Island Link (Both Poles) | 13.0899 | 0.0076 | 8e-05 | Note 5,7
Maritime Link | 1.417 | 0.02981 | 0.0002874 | Note 8,9
1Includes 1 MW of Holyrood station service losses
2For production plan Holyrood is modelled as net generation
3Includes 24 MW of Holyrood station service losses
4Updated to include MF - HVGB interconnection
5Includes 13.6 MW of SOP converter station losses
6Per Pole Loss Equation is used in the Reliability Model
7Both Pole Loss Equation is used in the Production/Expansion Model
8Includes 0.8 MW of Bottom Brook converter station losses
9Combined Equation for Line and Island Losses

## Expansion Options
Expansion Options
Plant Name | Capacity | Firm Capacity | Min Stable Generation | Heat Rate | Fuel Type | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Rate | Capital Cost1,2 | Fixed O&M1 | Variable O&M1 | Asset Life3
| MW | MW | MW | GJ/MWh |  | hrs | hrs | % | Weeks | $/kW | $/kW/year | $/MWh | years
CT - 141.6 MW | 141.6 | 141.6 | 35.4 | 9.167 | #2 Diesel - Hardwoods Price | 1 | 1 | 4.9 | 4 | 6297 | 21.13 | 6.34 | 45
CT - 94.4 MW | 94.4 | 94.4 | 23.6 | 9.167 | #2 Diesel - Hardwoods Price | 1 | 1 | 4.9 | 4 | 6889 | 21.13 | 6.34 | 45
CT - 47.2 MW | 47.2 | 47.2 | 11.8 | 9.167 | #2 Diesel - Hardwoods Price | 1 | 1 | 4.9 | 4 | 9857 | 21.13 | 6.34 | 45
CT - incremental 47.2 MW | 47.2 | 47.2 | 11.8 | 9.167 | #2 Diesel - Hardwoods Price | 1 | 1 | 4.9 | 4 | 8201 | 21.13 | 6.34 | 45
Portland Creek | 23 | 23 | 2.3 | - | - | 1 | 1 | 3.03 | 3 | 27682 | 125.85 | 8.33 | 70
Island Pond | 36 | 36 | 7.2 | - | - | 1 | 1 | 3.03 | 3 | 27372 | 127.8 | 8.33 | 70
Round Pond | 18 | 18 | 3.6 | - | - | 1 | 1 | 3.03 | 3 | 33499 | 151.57 | 8.33 | 70
BDE Unit 8 | 154.4 | 154.4 | - | - | - | 1 | 1 | 3.03 | 3 | 6200 | 17.06 | 8.33 | 70
Cat Arm Unit 3 | 68.2 | 68.2 | 16 | - | - | 1 | 1 | 3.03 | 3 | 8196 | 25.66 | 8.33 | 70
Wind 100 MW | 100 | See Wind ELCC tab | - | - | - | 1 | 1 | - | 1 | 2140 | 50 | 0 | 20
1All costs are in 2025 dollars
2Based on Rated Capacity.
3CT and Hydro asset life based on the 2022 Depreciation Study. Wind asset life based on the service life of existing wind farms @ Fermeuse & Stephenville.

## Wind ELCC
Wind Effective Load Carrying Capability
No. of 100 MW Units Added | Cumulative Installed Capacity (MW) | Incremental Firm Capacity1 (MW) | Incremental ELCC (%) | Cumulative ELCC (%)
1 | 100 | 40.5 | 40.5% | 40.5%
2 | 200 | 32 | 32% | 36.25%
3 | 300 | 22.5 | 22.5% | 31.67%
4 | 400 | 16.5 | 16.5% | 27.88%
5 | 500 | 13.8 | 13.8% | 25.06%
1. Based on 2025 ELCC Study.