## Sheet1
CA-NP-083 Attachment A Newfoundland Power Inc. - 2027 Capital Budget Application
Transformer | Age | Normal Degradation Index | Abnormal Thermal Index | Abnormal Electrical Index | Abnormal Core Index | DGA TCA Assessment | DGA TASA Assessment | Material Physical Findings | Customers Served | Spare Compatibility | Portable Compatibility | Last Major Maintenance | Risk Score | Proposed Dates | Cost
LAU-T1 | 50 | 0.58 | 0 | 0 | 0 | 1 | 1 | -Metal box welded to main tank to contain valve leak -Corrosion and rust present in many areas -LTC inoperable and unable to be repaired | 700 | 200219 200220 200385 | P1 P3 P4 P5 | 2025 | 16 | 2027-2028 | 3285000
LBK-T1 | 64 | 0.29 | 0.1 | 0 | 0 | 1 | N/A | -Radiators have advanced corrosion and repairs are unable to provide long term solution to leaks, radiators require complex replacement -Corrosion and rust present in many areas -Evidence of oil leakage at bushing base and main tank -Mechanical damage to high and low voltage bushings | Hydro Plant | - | P1 | 2009 | 16 | 2027-2029 | 2334000
HAR-T1 | 57 | 0.65 | 0.32 | 0 | 0 | 2 | N/A | - No notable corrosion or physical damage identified | 1400 | 200220 2000385 | P3 P4 P5 | 2023 | 16 | 2027-2029 | 2904000
RRD-T3 | 51 | 0.57 | 0 | 0 | 0 | 1 | N/A | -Corrosion and rust present in many areas | 4,400 (Shared) | 200385 | P3 P4 P5 | 2020 | 16 | 2027-2029 | 2695000